## Sheet1
Wiring details for REACCH Objective 2 monitoring stations
Base (mandatory) connections				Auxilary (optional) sensors
Device	Channel	Color	CR3000	Device	Channel	Color	CR3000
control box for / sonic, IRGA / (EC100)	SDM data	green	SDM-C1	N2O/CO analyzer / (Los Gatos)	N2O signal		DIFF 6H
	SDM clock	white	SDM-C2		N2O reference		DIFF 6L
	SDM enable	red	SDM-C3		CO signal		DIFF 7H
	SDM reference	black	G		CO reference		DIFF 7L
	SDM shield	clear	G	CO2/CH4 analyzer / (Picarro)	CH4 signal		DIFF 8H
	power in	red	Terminal strip		CH4 reference		DIFF 8L
	power ground	black			CO2 signal		DIFF 9H
Wind set / (034B)	WD signal	green	SE 11		CO2 reference		DIFF 9L
	WD excitation	blue	VX 1
	WD reference	white	earth
	WS signal	red	P1
	WS reference	black	earth
	shield	clear	earth
Temp/RH probe / (HMP-155A)	temp signal	yellow	DIFF 2H
	RH signal	blue	DIFF 3H
	signal reference	white	DIFF 2L + 3L
	power in	red	12V
	power ground	black	G
	shield	clear	earth
Rain gage / (TE 525)	rain signal	black	P2
	signal reference	white	earth
	shield	clear	earth
Net radiometer / (NR-Lite2)	net rad signal	red	DIFF 4H
	signal reference	blue	DIFF 4L + earth
	shield	black	earth
PAR sensor / (LI-190SB)	PAR signal	red	DIFF 5H
	signal reference	black	DIFF 5L + earth
	shield	clear	earth
GPS / (GPS16X-HVS)	msg trasmit (TX)	white	COM 4 Rx
	PPS	gray	COM 4 Tx
	receive data (RX)	blue	G
	shield	clear	G	Solar controller connections		Terminal strip connections
	power in	red	12V	Solar (+)	Solar panels (+)	(+)	CR3000	power 12V
	power ground	black	G	Solar (-)	Solar panels (-)		EC100	power 12V
	power switch	yellow	G	Battery (+)	Batteries (+)
Broadband modem / (RavenXT+SC105)	serial interface	-	CS I/O		Terminal strip (+)	(-)	CR3000	power G
	power in	red	12V	Battery (-)	Batteries (+)		EC100	power G
	power ground	black	G		Terminal strip (-)